|  |  |  |
| --- | --- | --- |
| BOARD OF EDUCATION  Mrs. Patricia Lock-Dawson,  President  Dr. Angelov Farooq,  Vice President  Mrs. Kathy Allavie,  Clerk  Mr. Tom Hunt  Mr. Brent Lee  Members | Riverside Unified School District  OPERATIONS DIVISION  3070 WASHINGTON STREET  RIVERSIDE, CALIFORNIA 92504  MAINTENANCE & OPERATIONS  (951) 788-7496 X84001  FAX: (951) 778-5646 | DAVID C. HANSEN, ED.D.  District Superintendent  New Image |

**SUBJECT: LEAD SAMPLING RESULTS - Abraham Lincoln Continuation**

On October 13th, 2017, California Assembly Bill 746 Section 116277 of the Health and Safety Code (HSC 116277) was passed, mandating the lead testing of community water systems for all public Kindergarten through grade 12 (K-12), preschools and child day care facilities before July 1st. 2019.

In California, the State Water Resources Control Board (SWRCB) oversees public water systems to ensure the water they provide is tested and safe according to the regulations set forth by the State and Federal Safe Drinking Water Acts. Regulations pursuant to those acts include a regulation adopted by the United States Environmental Protection Agency (USEPA) and the SWRCB to control lead levels in drinking water. Lead in drinking water is typically found at its highest levels upon a *first draw.* A first draw is a sampling of water taken from a fixture after the water has been stagnated for an extended period of time, i.e., overnight. Each sample taken at sample locations are taken as a first draw in order to capture and record the highest level present at a sampling location.

On December 4th, 2018, Riverside Public Utilities collected water samples at 5 locations throughout the site. Below are the laboratory results of those samples.

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| Sample | Fixture type | Location | Action Level | Result |
| 1 | Drinking Fountain | B Wing Ext. Rm 7 Near RR’s Tall Left | Below | ND |
| 2 | Drinking Fountain | C Wing Ext. Hallway Near Rm 6 | Below | 7.1ppb |
| 3 | Drinking Fountain | D Wing Ext. Hallway Near Rm 3 | Below | ND |
| 4 | Drinking Fountain | F Wing Exterior of Gym Middle Unit | Below | 8.1ppb |
| 5 | Drinking Fountain | Main Office Interior | Below | ND |

*\*ND= Not detected, ppb=part per billion (equivalent to approx. 1 water drop in an Olympic size pool)*